## Slide 1
Relative age prediction of wind turbines
with random forests
Arne Deloose, Bernard De Baets, Jan Verwaeren
arne.deloose@ugent.be, bernard.debaets@ugent.be, jan.verwaeren@ugent.be
Introduction
Wind turbine challenges:
Difficult to perform maintenance (especially off-shore)
High installation costs
=> optimize lifespan via data analysis
We measure two kinds of variables on the wind turbines:
Weather variables
Technical variables (on different parts of the turbine)
Weather correction
We are mainly interested in the technical variables. However, these will be influenced by the weather. To deal with this, we will correct the original variables with the weather variables. Two examples are given below.
Random forests
24 technical variables are measured four times (min, max, std and av)=> difficult to know what to focus on
Solution: random forest regressor
Random forest regressor: collection of regression trees that are a variant of decision trees
Left figure:
Original hub temperature => corrected hub temperature
One year, measurements every 10 min => 52 560 datapoints
Hub is outside=> responds heavily to weather. Summer=warm, winter=cold
Use weather to correct variable blue=> orange
Remaining variance not explained by weather=> possible indication something is wrong (anomaly)
Right figure:
Generator bearing temperature
Inside=> less response to weather
Minimum value: bounded by outside weather (cannot get colder)
Maximum: not bounded by weather (can get warmer)
Corrected variable: pushed up slightly in winter when it’s low
Relative age vs real age
Weather filtered out
Remaining variance=> age/condition
Condition goes down over time (see patterns below)
Real condition: hard to measure=> use relative age
Select turbine and link real time to condition
Apply this to other turbines
If predicted age< real age => better condition than expected
If predicted age> real age => worse than expected=> flag for maintenance
Left (decision tree):
Variables: age, pizza eating and exercising=> fit or unfit
Follow tree down to specific nodes
Limited because only two outcomes=> more complex versions
Right (regression tree):
More complex
Nodes-> regions with a specific function (x1: age, x2: exercise)
Fitness=number
Health for low age: f1(exercise, eating)
Health for high age and low exercise: f2(exercise, eating, age)
Health for high age and high exercise: f3(exercise, age)
Turbines:
Learn regions and functions
Combine multiple trees=> more robust
Average outcome of individual trees (see figure below)
Fit on one turbine, apply on others:
Results
Check importance variables
Model always selects best variable to make split
Count splits in all trees
Five most important ones (importance sums to 1)
Nacelle temperature std: 0.18 (variation in temperature of the casing, heat production)
Power factor min: 0.11 (kind of efficiency)
Grid voltage: 0.04 (important for disconnection)
Generator stator temperature min: 0.04 (heat production)
Rotor bearing temperature max: 0.04 (heat production)
x-axis: real age, y-axis: predicted age (in days)
Green: ideal case (perfect prediction), blue: individual predictions, orange: rolling average over one month
Limited accuracy (large deviations between individual days).
Monthly average: increases relatively smoothly
=> One month of data=> reasonably accurate prediction
Relative age too high=> indication of bad condition, too low=> good condition
=> prioritize bad condition turbines
Importance variables
Take home message
Weather and age are the two most important sources of variance
Relative age/condition of a wind turbine can be determined. One month of data is sufficient
Random forests can successfully find which variables are important
Most important factors for aging are: heat production, disconnection and electrical efficiency